## Worksheet
ledbetter
Project Name:
Date:
Unit Designation:
A | B | C | D | E | F | G | H | I | J | K | L | M | N | O
Room | Description | Area (ft²) (Az) | Area Outdoor Air Rate per VMC Table 403.3 (Ra) | Area Outdoor Air (RaAz) | Occupant Load Rate per VMC Table 403.3 (People/ 1000 ft2) | Occupancy C x F/1000 (Pz) | Occupant Outdoor Air Rate per VMC Table 403.3 (Rp) | Occupant Outdoor Air (RpPz) | Breathing Zone Outdoor Air (Vbz = RpPz + RaAz) | Zone Air Distribution Effectiveness (Ez) | Zone Outdoor Air (Voz = Vbz / Ez) | Supply Air Design (Vpz) | Transfer Air | Outdoor Air Fraction (Zp = Voz / Vpz)
|  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0.0001 | 0.0001 | 0
|  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0.0001 | 0.0001 | 0
|  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0.8 | 0 | 0.0001 | 0.0001 | 0
Totals |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 | 0.0003 | 0.0003 | 0
2006 OA Version 5.5 - FFX - REG - 3/15/09 |  |  |  |  | Occupant Diversity D = Ps/∑all zones Pz | [8 empty] | Ev
[9 empty] | Total Required Outdoor Air |  |  |  |  | 1
Do not utilize Occupant Diversity without specific approval from the Authority Having Jurisdiction
[6 empty] | #DIV/0! |  |  |  | #DIV/0!
Uncorrected O.A. Vou = D ∑all zones RpPz + ∑all zones RaAz
| System Population (Ps) | [7 empty] | Percentage of Outdoor Air
| Diversity → | 0 |  |  |  | #DIV/0! |  |  |  | #DIV/0!
Note on C24: Without diversity, this cell must equal cell G Total. With diversity, enter the new occupant load into this cell.
Note on G12: Use this cell to manually insert occupant loads where actual occupant loads differ from those found in Table 403.3
Note on B10: Row Type 1 (auto) See instructions tab
Note on B11: Row Type 2 (manual) See instructions tab
Note on B12: Row Type 3 (insert occupancy) See instructions tab
Note on K10: See IMC Table 403.3.1.2 for applicable rates.
Note on K11: See IMC Table 403.3.1.2 for applicable rates.
Note on K12: See IMC Table 403.3.1.2 for applicable rates.

## Definitions
Minimum Ventilation Rates from IMC Table 403.3
| Space | Rp (cfm/pers.) | Ra (cfm/sqft) | Default Occ. Den. #/1000 sqft | Zone Air Distribution Effectiveness per VMC Table 403.3.1.2 (Ez)
Correctional Facility | Cell | 5 | 0.12 | 25 | 1 | Ceiling or floor supply of cool air / Ceiling or floor supply of warm air and floor return
| Booking | 7.5 | 0.06 | 50 | 0.8 | Ceiling supply of warm air and ceiling return / Makeup air drawn in on the opposite side of the room from the exhaust and/or return
| Booking rm | 7.5 | 0.06 | 50 | 0.7 | Floor supply of warm air and ceiling return
| Booking room | 7.5 | 0.06 | 50 | 0.5 | Makeup air drawn in near to the exhaust and/or return location
| Day rm | 5 | 0.06 | 30
| Day room | 5 | 0.06 | 30
| Guard station | 5 | 0.06 | 15 | System Ventilation Efficiency per VMC Table 403.3.2.3.2 (Ev)
| Waiting | 7.5 | 0.06 | 50 | Any Zp < 0.15 will have an Ev equal to 1.0
| Waiting rm | 7.5 | 0.06 | 50
| Waiting room | 7.5 | 0.06 | 50 | Max Zp | Ev
Dry cleaners, laundries | Coin-operated dry cleaner | 15 | 0 | 20 |  |  | Drop Down Menu Values
| Coin-operated laundry | 7.5 | 0.06 | 20 | 0.05 | 1
| Commercial dry cleaner | 30 | 0 | 30 | 0.06 | 1 | Ol | Rp | Ra
| Commercial laundry | 25 | 0 | 10 | 0.07 | 1 | 0 | 0 | 0
| Storage, pick up | 7.5 | 0.12 | 30 | 0.08 | 1 | 4 | 5 | 0.06
Education | Art classroom | 10 | 0.18 | 20 | 0.09 | 1 | 5 | 7.5 | 0.12
| Art rm | 10 | 0.18 | 20 | 0.1 | 1 | 8 | 10 | 0.18
| Art room | 10 | 0.18 | 20 | 0.11 | 1 | 10 | 15 | 0.3
| Auditorium | 5 | 0.06 | 150 | 0.12 | 1 | 15 | 20 | 0.48
| Chemistry | 10 | 0.18 | 25 | 0.13 | 1 | 20 | 25
| Chemistry room | 10 | 0.18 | 25 | 0.14 | 1 | 25 | 30
| Classroom | 10 | 0.12 | 35 | 0.15 | 1 | 30 | 60
| Classroom 5-8 | 10 | 0.12 | 25 | 0.155 | 0.99 | 35
| Classroom 9+ | 10 | 0.12 | 35 | 0.16 | 0.99 | 40
| Computer lab | 10 | 0.12 | 25 | 0.165 | 0.98 | 50
| Dance | 10 | 0.06 | 35 | 0.17 | 0.98 | 60
| Dance rm | 10 | 0.06 | 35 | 0.175 | 0.97 | 65
| Dance room | 10 | 0.06 | 35 | 0.18 | 0.97 | 70
| Daycare | 10 | 0.18 | 25 | 0.185 | 0.96 | 100
| Lecture classroom | 7.5 | 0.06 | 65 | 0.19 | 0.96 | 120
| Lecture hall | 7.5 | 0.06 | 150 | 0.195 | 0.95 | 150
| Media center | 10 | 0.12 | 25 | 0.2 | 0.95
| Metal Shop | 10 | 0.18 | 20 | 0.205 | 0.94
| Music | 10 | 0.06 | 35 | 0.21 | 0.94
| Music rm | 10 | 0.06 | 35 | 0.215 | 0.93
| Music room | 10 | 0.06 | 35 | 0.22 | 0.93
| Science Lab | 10 | 0.18 | 25 | 0.225 | 0.92
| Shop | 10 | 0.18 | 20 | 0.23 | 0.92
| Smoking lounge | 60 | 0 | 70 | 0.235 | 0.91
| Smoking rm | 60 | 0 | 70 | 0.24 | 0.91
| Smoking room | 60 | 0 | 70 | 0.245 | 0.9
| Theater | 10 | 0.06 | 35 | 0.25 | 0.9
| Wood Shop | 10 | 0.18 | 20 | 0.255 | 0.89
Food and beverage service | Bar | 7.5 | 0.18 | 100 | 0.26 | 0.89
| Bar room | 7.5 | 0.18 | 100 | 0.265 | 0.88
| Café | 7.5 | 0.18 | 70 | 0.27 | 0.88
| Cafeteria | 7.5 | 0.18 | 100 | 0.275 | 0.87
| Cocktail lounge | 7.5 | 0.18 | 100 | 0.28 | 0.87
| Dining | 7.5 | 0.18 | 70 | 0.285 | 0.86
| Dining hall | 7.5 | 0.18 | 70 | 0.29 | 0.86
| Dining room | 7.5 | 0.18 | 70 | 0.295 | 0.85
| Fast food | 7.5 | 0.18 | 100 | 0.3 | 0.85
| Lounge | 7.5 | 0.18 | 100 | 0.305 | 0.84
Hospitals, nursing, and convalescent homes | Dental | 15 | 0 | 20 | 0.31 | 0.84
| Dental chair | 15 | 0 | 20 | 0.315 | 0.83
| Dental room | 15 | 0 | 20 | 0.32 | 0.83
| ICU | 15 | 0 | 20 | 0.325 | 0.82
| ICU room | 15 | 0 | 20 | 0.33 | 0.82
| Medical procedure room | 15 | 0 | 20 | 0.335 | 0.81
| Operating room | 30 | 0 | 20 | 0.34 | 0.81
| Patient room | 25 | 0 | 10 | 0.345 | 0.8
| Physical recovery | 15 | 0 | 20 | 0.35 | 0.8
| Physical therapy | 15 | 0 | 20 | 0.355 | 0.79
| Recovery | 15 | 0 | 20 | 0.36 | 0.79
| Recovery room | 15 | 0 | 20 | 0.365 | 0.78
Hotels, motels, resorts, and dormitories | Assembly | 5 | 0.06 | 120 | 0.37 | 0.78
| Assembly rm | 5 | 0.06 | 120 | 0.375 | 0.77
| Assembly room | 5 | 0.06 | 120 | 0.38 | 0.77
| Bedroom | 5 | 0.06 | 10 | 0.385 | 0.76
| Casino | 7.5 | 0.18 | 120 | 0.39 | 0.76
| Conference | 5 | 0.06 | 50 | 0.395 | 0.75
| Conference rm | 5 | 0.06 | 50 | 0.4 | 0.75
| Conference room | 5 | 0.06 | 50 | 0.405 | 0.74
| Dorm sleeping area | 5 | 0.06 | 20 | 0.41 | 0.74
| Dormitory sleeping area | 5 | 0.06 | 20 | 0.415 | 0.73
| Gambling casino | 7.5 | 0.18 | 120 | 0.42 | 0.73
| Living rm | 5 | 0.06 | 10 | 0.425 | 0.72
| Living room | 5 | 0.06 | 10 | 0.43 | 0.72
| Meeting | 5 | 0.06 | 50 | 0.435 | 0.71
| Meeting rm | 5 | 0.06 | 50 | 0.44 | 0.71
| Meeting room | 5 | 0.06 | 50 | 0.445 | 0.7
| Multi-purpose assembly | 5 | 0.06 | 120 | 0.45 | 0.7
| Multi-purpose rm | 5 | 0.06 | 120 | 0.455 | 0.69
| Multi-purpose room | 5 | 0.06 | 120 | 0.46 | 0.69
| Pre-function area | 7.5 | 0.06 | 30 | 0.465 | 0.68
| Pre-function rm | 7.5 | 0.06 | 30 | 0.47 | 0.68
| Pre-function room | 7.5 | 0.06 | 30 | 0.475 | 0.67
| Sleeping area | 5 | 0.06 | 20 | 0.48 | 0.67
Offices | Break | 5 | 0.06 | 5 | 0.485 | 0.66
| Break rm |  |  |  | 0.49 | 0.66
| Break room |  |  |  | 0.495 | 0.65
| Breakout | 7.5 | 0.06 | 30 | 0.5 | 0.65
| Breakout rm |  |  |  | 0.505 | 0.64
| Breakout room |  |  |  | 0.51 | 0.64
| Data entry | 5 | 0.06 | 60 | 0.515 | 0.63
| Galley | 5 | 0.06 | 5 | 0.52 | 0.63
| Huddle | 5 | 0.06 | 50 | 0.525 | 0.62
| Huddle rm | 5 | 0.06 | 50 | 0.53 | 0.62
| Huddle room | 5 | 0.06 | 50 | 0.535 | 0.61
| Main entry lobby | 5 | 0.06 | 10 | 0.54 | 0.61
| Main lobby | 5 | 0.06 | 10 | 0.545 | 0.6
| Office | 5 | 0.06 | 5 | 0.55 | 0.6
| Open area | 5 | 0.06 | 5 | 0.555 | 0.59
| Open office | 5 | 0.06 | 5 | 0.56 | 0.59
| Pantry | 5 | 0.06 | 5 | 0.565 | 0.58
| Reception | 5 | 0.06 | 30 | 0.57 | 0.58
| Reception area | 5 | 0.06 | 30 | 0.575 | 0.57
| Team | 5 | 0.06 | 50 | 0.58 | 0.57
| Team rm | 5 | 0.06 | 50 | 0.585 | 0.56
| Team room | 5 | 0.06 | 50 | 0.59 | 0.56
| Training |  |  |  | 0.595 | 0.55
| Training rm |  |  |  | 0.6 | 0.55
| Training room |  |  |  | 0.605 | 0.54
Public Spaces | Chambers | 5 | 0.06 | 50 | 0.61 | 0.54
| Corridors | 0 | 0.06 | 0 | 0.615 | 0.53
| Courtroom | 5 | 0.06 | 70 | 0.62 | 0.53
| Fellowship hall | 5 | 0.06 | 120 | 0.625 | 0.52
| Gallery | 7.5 | 0.06 | 40 | 0.63 | 0.52
| Hall | 5 | 0.06 | 120 | 0.635 | 0.51
| Hallway | 0 | 0.06 | 0 | 0.64 | 0.51
| Legislative chambers | 5 | 0.06 | 50 | 0.645 | 0.5
| Library | 5 | 0.12 | 10 | 0.65 | 0.5
| Museum | 7.5 | 0.06 | 40 | 0.655 | 0.49
| Museum children | 7.5 | 0.12 | 40 | 0.66 | 0.49
| Narthex | 7.5 | 0.06 | 30 | 0.665 | 0.48
| Places of religious worship | 5 | 0.06 | 120 | 0.67 | 0.48
| Sanctuary | 5 | 0.06 | 120 | 0.675 | 0.47
Retail Stores | Mall common area | 7.5 | 0.06 | 40 | 0.68 | 0.47
| Receiving | 0 | 0.12 | 0 | 0.685 | 0.46
| Retail | 7.5 | 0.12 | 15 | 0.69 | 0.46
| Retail area | 7.5 | 0.12 | 15 | 0.695 | 0.45
| Sales | 7.5 | 0.12 | 15 | 0.7 | 0.45
| Sales area | 7.5 | 0.12 | 15 | 0.705 | 0.44
| Shipping | 0 | 0.12 | 0 | 0.71 | 0.44
| Stock | 0 | 0.12 | 0 | 0.715 | 0.43
| Stock rm | 0 | 0.12 | 0 | 0.72 | 0.43
| Stock room | 0 | 0.12 | 0 | 0.725 | 0.42
| Storage | 0 | 0.12 | 0 | 0.73 | 0.42
| Storage area | 0 | 0.12 | 0 | 0.735 | 0.41
| Storage rm | 0 | 0.12 | 0 | 0.74 | 0.41
| Storage room | 0 | 0.12 | 0 | 0.745 | 0.4
Specialty Shops | Barber | 7.5 | 0.06 | 25 | 0.75 | 0.4
| Barber shop | 7.5 | 0.06 | 25 | 0.755 | 0.3
| Beauty salon | 20 | 0.12 | 25 | 0.76 | 0.3
| Color mixing |  |  |  | 0.77 | 0.3
| Color mixing rm |  |  |  | 0.78 | 0.3
| Color mixing room |  |  |  | 0.79 | 0.3
| Facial |  |  |  | 0.8 | 0.3
| Facial rm |  |  |  | 0.81 | 0.3
| Facial room |  |  |  | 0.82 | 0.3
| Nail salon | 20 | 0.12 | 25 | 0.83 | 0.3
| Pet shop | 7.5 | 0.18 | 10 | 0.84 | 0.3
| Shampoo |  |  |  | 0.85 | 0.3
Shampoo rm
Shampoo room
| Supermarket | 7.5 | 0.06 | 8
Tanning
Tanning rm
Tanning room
Tanning salon
Wax
Wax rm
Wax room
Sports and Amusement | Aerobics | 20 | 0.06 | 40
| Aerobics rm | 20 | 0.06 | 40
| Aerobics room | 20 | 0.06 | 40
| Arcade | 7.5 | 0.18 | 20
| Arena | 0 | 0.3 | 0
| Bowling alley | 10 | 0.12 | 40
| Dance area | 20 | 0.06 | 100
| Dance floor | 20 | 0.06 | 100
| Disco | 20 | 0.06 | 100
| Fitness | 20 | 0.06 | 40
| Fitness rm | 20 | 0.06 | 40
| Fitness room | 20 | 0.06 | 40
| Game arcade | 7.5 | 0.18 | 20
| Gym | 0 | 0.3 | 0
| Gymnasium | 0 | 0.3 | 0
| Health club/aerobics | 20 | 0.06 | 40
| Health club/aerobics rm | 20 | 0.06 | 40
| Health club/aerobics room | 20 | 0.06 | 40
| Health club/weight | 20 | 0.06 | 10
| Health club/weight rm | 20 | 0.06 | 10
| Health club/weight room | 20 | 0.06 | 10
| Ice arena | 0 | 0.3 | 0
| Pool | 0 | 0.48 | 0
| Pool deck | 0 | 0.48 | 0
| Spectator | 7.5 | 0.06 | 150
| Spectator area | 7.5 | 0.06 | 150
| Stadium | 0 | 0.3 | 0
| Swimming pool | 0 | 0.48 | 0
| Weight rm | 20 | 0.06 | 10
| Weight room | 20 | 0.06 | 10
Storage | Warehouse | 0 | 0.06 | 0
Theaters | Lobby | 5 | 0.06 | 150
| Stage | 10 | 0.06 | 70
| Studio | 10 | 0.06 | 70
| Ticket booth | 5 | 0.06 | 60
Transportation | Platforms | 7.5 | 0.06 | 100
| Transportation waiting | 7.5 | 0.06 | 100
Workrooms | Bank vault | 5 | 0.06 | 5
| Computer | 5 | 0.06 | 4
| Computer rm | 5 | 0.06 | 4
| Computer room | 5 | 0.06 | 4
| Copy | 5 | 0.06 | 4
| Copy rm | 5 | 0.06 | 4
| Copy room | 5 | 0.06 | 4
| IT | 5 | 0.06 | 4
| IT rm | 5 | 0.06 | 4
| IT room | 5 | 0.06 | 4
| Lan | 5 | 0.06 | 4
| Lan rm | 5 | 0.06 | 4
| Lan room | 5 | 0.06 | 4
| Meat processing | 15 | 0 | 10
| Pharmacy | 5 | 0.18 | 10
| Photo studio | 5 | 0.12 | 10
| Photostudio | 5 | 0.12 | 10
| Printing | 5 | 0.06 | 4
| Printing rm | 5 | 0.06 | 4
| Printing room | 5 | 0.06 | 4
| Server | 5 | 0.06 | 4
| Server rm | 5 | 0.06 | 4
| Server room | 5 | 0.06 | 4
| Vault | 5 | 0.06 | 5

## Instructions
Macros must be enabled for the "Add Rows" and "Delete Rows" buttons to work. If you are experiencing trouble with the macro, either check with your IT personnel or go to the "Tools" button, then "Macro", then "Security. In the Security window that pops up, click on the tab for "Trusted Publishers". Make sure that "Trust access to Visual Basic Project" is checked. You may also have to lower the Security Level to "medium" to enable the macro. Shut down Excel (not the computer) and restart after changing the settings.
This spreadsheet is for use with multi-zone recirculating systems only. Do not use this spreadsheet for single-zone systems or 100% outdoor air systems. See IMC 403.3.2 as amended by the Virginia Uniform Statewide Building Code (USBC).
The user must fill in the room number (column A), the room description (column B), the room area in square feet (column C), the supply air design (column M) and transfer air (if applicable, column N, see Transfer Air note below) for each room. "Project Name", "Date", and "Unit Designation" must be used when multiple units are calculated for a single project. NOTE: You must put in a numerical figure in column M (supply air) of at least 0.0001 for the formulas to calculate correctly, even where no supply air is being provided to a space.
There are three different types of rows that can be added/deleted to/from the worksheet: Row type 1 will automatically input columns D (area outdoor air rate), F (occupant load rate) and H (occupant outdoor air rate) when a common room description is inserted in column B. Common room descriptions from IMC Table 403.3 can be found in the "Definitions" tab of this workbook. Row type 2 requires the user to manually input columns D (area outdoor air rate), F (occupant load rate) and H (occupant outdoor air rate) from a drop down menu provided when a similar room description cannot be found in IMC Table 403.3. Row type 3 requires the user to manually input the occupant load in column G when the actual or reasonable occupant load does not correspond with IMC Table 403.3. (Example 1 - 1,000 square open office calculates 5 occupants per Table 403.3. Room is actually designed with 15 workstations. 15 occupants must be manually inserted into column G. Example 2 - The worksheet will automatically calculate 2 occupants for an office space exceeding 200 square feet. It is not unreasonable to change this to 1 occupant for a 250 square foot office space. This can make a huge difference on a system that serves 20 or 30 of these types of large office spaces)
Where VAV's are utilized to provide ventilation air to a room, the supply airflow shown in column M must be the lowest expected rate when the room is fully occupied (IMC 403.3.2.3.1). When other than the minimum VAV set points are used in column M, details must be provided on the plans showing control devices, and the sequence of operation of such devices, that will have the ability of maintaining the flow rate of outdoor air across the entire range of supply air operating rates (IMC 403.6).
Transfer Air - Where outdoor air is provided to a space that is in excess of that required by IMC Table 403.3, such air may be transferred to other spaces as a component of supply air to the second space (IMC 403.2.1).